## ADA & Accessibility
Rule ID | What To Check | Fail When | Severity | Code Ref | How To Fix | When To Apply
A-101 | Door in Path of Egress | < 32" | Critical | IBC 1010.1.1 / ADA | Increase door leaf size or revise configuration to achieve minimum 32" clear. | ada_required=true
A-102 | Exterior Door | > 1/2" | Moderate | ADA 404 | Provide ramped threshold or adjust exterior slab. | ada_required=true, location=exterior
A-103 | Hardware mounting height | Not between 34"–48" | Moderate | ADA / ICC A117.1 | Relocate hardware within 34"–48" AFF. | ada_required=true
A-104 | Operable force | > code limit | Moderate | ADA / ICC A117.1 | Specify hardware within allowable force limits. | ada_required=true
A-105 | Non-accessible operable parts | Tight grasp required | Moderate | ADA / ICC A117.1 | Replace with lever or accessible hardware. | ada_required=true
A-106 | Door opening force | Exceeds limits | Moderate | ADA / ICC A117.1 | Reduce closer force or change hardware. | ada_required=true
A-107 | Door in Path of Egress | Hardware set calls for latching hardware with no panic | Critical |  | Use egress hardware set with exit device

## Fire & Life Safety
Rule ID | What To Check | Fail When | Severity | Code Ref | How To Fix | When To Apply
F-101 | Fire Rated Door | Not Shown | Critical | IBC 715 / NFPA 80 | Provide listed fire-rated glazing assembly. | fire_rated=true
F-102 | Door in Path of Egress | Not Shown | Moderate | NFPA 80 | Provide self-closing, positive-latching hardware. | fire_rated=true
F-103 | Self-closing / positive latching | Not provided | Critical | NFPA 80 / IBC | Provide self-closing, positive-latching hardware. | fire_rated=true
F-104 | Fire door hardware listing | Not shown | Critical | NFPA 80 / UL10C | Specify hardware listed for fire-rated door assembly. | fire_rated=true
F-105 | Fire rated door with access control | No fire-rated exit device | Critical | NFPA 80 / IBC | Provide fire-rated electrified exit device. | fire_rated=true, access_control=true
F-106 | Fire alarm interface | Not documented | Warning | NFPA 72 / NFPA 80 | Document fire alarm unlock interface. | fire_rated=true
F-107 | Door Vision Lite | Not Shown | Critical | IBC 2406.4.1 | Specify safety glazing meeting ANSI Z97.1 / 16 CFR 1201. | glazing=true
F-108 | Adjacent Glazing | Within 24" | Critical | IBC 2406.4.2 | Provide safety glazing at sidelites within 24" of door. | glazing=true
F-109 | Fixed Glazing Panel | Area > 9 SF | Moderate | IBC 2406.4.3 | Upgrade panel to safety glazing. | glazing=true

## Egress
Rule ID | What To Check | Fail When | Severity | Code Ref | How To Fix | When To Apply
E-101 | Door in Path of Egress | < 80" | Moderate |  | Increase clear height or adjust closer/stop. | egress=true
E-102 | Required Panic Hardware | Occupancy + occupant load | Critical | IBC / NFPA | Provide panic or fire exit hardware listed per ANSI/BHMA A156.3. | egress=true, panic_required=true
E-103 | Delayed egress device | Not permitted | Moderate | IBC / NFPA | Remove delayed egress unless specifically allowed. | egress=true
E-104 | Additional locking devices | Present | Critical | IBC / NFPA | Remove secondary locks or chains. | egress=true
E-105 | Electrified lock on egress door | Fail-secure | Critical | IBC / NFPA | Change electrified lock to fail-safe configuration. | egress=true, electrified=true
E-106 | Electrified lock release | Not tied to fire alarm | Critical | IBC / NFPA | Integrate lock release with fire alarm system. | egress=true, electrified=true
E-107 | Electrified lock on egress door | No manual release | Critical | IBC / NFPA | Add manual push-to-exit or panic release. | egress=true, electrified=true
E-108 | Stairwell door locking | Does not unlock on fire alarm | Critical | IBC | Configure stair doors to unlock upon fire alarm. | egress=true, stairwell=true
E-109 | Stairwell door re-entry | No re-entry provision | Critical | IBC | Add fail-safe unlocking or remote release. | egress=true, stairwell=true
E-110 | Power transfer device | Not specified | Warning | Field Practice (Non-Code) | Add power transfer or electric hinge. | electrified=true
E-111 | Access controlled exterior door | No free egress | Critical | IBC / ADA | Provide free mechanical egress regardless of credentialing. | egress=true, access_control=true, location=exterior
E-112 | Vestibule access sequence | Exterior door controlled | Critical | Field Practice (Non-Code) | Move access control to interior vestibule doors. | vestibule=true, location=exterior
E-113 | Actuating portion width | < 1/2 door width | Moderate | ANSI/BHMA A156.3 | Specify panic device with pad/bar ≥ 1/2 door leaf width. | panic_required=true
E-114 | Access control with panic hardware | Improper combination | Critical | IBC / NFPA / ADA | Provide electrified panic hardware listed for access control. | panic_required=true, access_control=true
E-115 | Panic hardware with electric strike | Improper configuration | Moderate | Field Practice (Non-Code) | Replace with electrified exit device or latch retraction. | panic_required=true

## Automatic Operators
Rule ID | What To Check | Fail When | Severity | Code Ref | How To Fix | When To Apply
O-101 | Door with Auto Operator | Not Shown | Moderate | ADA 404 | Coordinate power, sensors, push plates, and clearances. | auto_operator=true
O-102 | Door closer + operator conflict | Unbalanced opening force | Moderate | ADA / Field Practice | Adjust closer spring size or operator settings. | auto_operator=true
O-103 | Air pressure across door | Prevents proper closing | Moderate | Field Practice (Non-Code) | Rebalance HVAC pressure or upgrade closer. | auto_operator=true
O-104 | Door does not fully close or latch | Present | Critical | NFPA 80 / IBC | Increase closer strength or adjust air balance. | auto_operator=true

## Door Hardware
Rule ID | What To Check | Fail When | Severity | Code Ref | How To Fix | When To Apply
H-101 | Vestibule Condition | Not Shown | Advisory | Field Practice (Non-Code) | Exterior doors latch; interior doors handle access control. | vestibule=true
H-102 | Exterior Door | Not Shown | Advisory | Field Practice (Non-Code) | Provide latching hardware even in vestibule conditions. | location=exterior
H-103 | Door with Access Control | Not Shown | Warning | Field Practice (Non-Code) | Complete hardware schedule. | access_control=true
H-104 | Hardware set incomplete | Not fully specified | Warning | Field Practice (Non-Code) | Complete hardware set.
H-105 | Hardware model number function | Function compliance | Warning | Field Practice (Non-Code) | Provide alternate function

## MA Specific
Rule ID | What To Check | Fail When | Severity | Code Ref | How To Fix | When To Apply
R-005 | Door with Auto Operator | < 80" | Moderate | MA 780 CMR | Raise closer to minimum 80" AFF to lowest component. | state=MA, auto_operator=true
R-013 | Door Vision Lite | Not Shown | Moderate | MA 780 CMR 2406.2 | Add manufacturer safety glazing label callouts. | state=MA, glazing=true

## Aluminum Door Stile Widths
Vendor | Model | Series | Stile Width | Depth
Kawneer | Insulpour | 250T | 2.5" | 2.25"
Kawneer | Insulpour | 350T | 3.5" | 2.25"
Kawneer | Insulpour | 500T | 5" | 2.25"
Kawneer | Standard | 190.0 | 2.125" | 1.75"
Kawneer | Standard | 350.0 | 3.5" | 1.75"
Kawneer | Standard | 500.0 | 5" | 1.75"
YKK |  | 20D | 2.125"
YKK |  | 35D | 3.5"
YKK |  | 50D | 5"
YKK |  | 25T | 2.5" | 2"
YKK |  | 35T | 3.5" | 2"
YKK |  | 50T | 5" | 2"
CRL |  | 250.0
CRL |  | 400.0
CRL |  | 550.0
CRL |  | 250T
CRL |  | 400T
CRL |  | 550T
OldCastle |  | NS-212
OldCastle |  | MS-375
OldCastle |  | WS-500
OldCastle |  | MS-375TC
OldCastle |  | WS-500TC
Tubelite | Standard | Narrow | 2.125"
Tubelite | Standard | Medium | 4"
Tubelite | Standard | Wide | 5"
Tubelite | ThermalBlock | Medium | 4"
Tubelite | ThermalBlock | Wide | 5"
FHC